SAMPLE SPECIFICATIONS

FOR A

STEEL WEATHER PROTECTIVE ENCLOSURE

SCOPE

The requirements contained in this specification shall apply to and govern the work under this section.

WORK INCLUDED:

Provide labor and materials necessary to install a weather protective standby diesel engine-generator set of the latest commercial type and design and as specified herein.

SUBSTITUTIONS:

To ensure a fair and equitable opportunity for all bidders, requests for substitution of materials shall be made a minimum of ten days prior to bid date and manufacturers catalog data shall accompany each request. Upon review of the materials received, and provided the substitution of materials is acceptable to the engineer, authorized acceptance shall be made by published addendum only. The published addendum shall be made available to all bidders.

EXPERIENCE:

Only generator set suppliers or vendors who have a minimum of fifteen years experience in the field of power generation, and can certify to this requirement, are allowed to furnish equipment for this project.

SUBMITTALS:

The contractor shall furnish information showing manufacturer’s model numbers, dimensions and weights for the engine, generator, enclosure, and major auxiliary equipment. All drawing and wiring schematics must be available in AutoCAD format and all component catalog cut-sheets must be available in PDF format.

PRODUCT

WEATHER PROTECTIVE ENCLOSURE:

Intent - The intent of this specification is to provide the owner with a weather protective generator set enclosure complete in every detail and requiring no additional in-field modifications or assembly, except where specifically allowed by these specifications. The enclosure is to be accurately dimensioned so as to be in compliance with the National Electrical Code (NEC), and the National Fire Protection Association (NFPA) for clearance of all specified items included therein, and all applicable fire codes for a structure and application of this type.

Drawings - Construction drawings, engineering blueprints, or other bid documents accompanying these specifications which show switchgear, transfer switch(es), motor controllers, and/or other service or distribution equipment, etc., within the generator set enclosure must be considered complimentary to and not in lieu of this written specification. Drawings submitted for approval shall reflect this fact clearly and any contradiction or omission shall be brought to the attention of the designing engineer prior to bid.

Construction - The weather protected enclosure shall be of formed steel construction as designed and manufactured by Chillicothe Metal Company, Inc. (CMCO).  The design and construction shall be modular in that the side panels and doors shall not exceed 36” in width and shall be a minimum thickness of 14 gauge for all component parts. The roof of the enclosure shall meet or exceed the minimum gauge requirements specified but, in addition, shall be strengthened in such a manner as to support the largest commercially available exhaust silencer recommended by the engine manufacturer for this application.

Doors - All doors on the enclosure shall be strategically located in areas as to allow ease of maintenance on the generator set and allow good access to and visibility of instruments, controls, engine gauges, etc. The doors shall be fitted with bolt-on, stainless steel constructed strap type hinges. Each door shall be fitted with a stainless steel constructed flush-mounted, adjustable, keylock latches.

Louvers - All louvers shall have sufficient free area to allow for 120% of the total engine/generator cooling air requirements used in this application. Louvers shall be of all galvanized construction and shall be motorized to open when the generator runs, and close when the generator stops.

Sound Attenuation - The entire enclosure except for the louvered openings shall have sound attenuation material mechanically attached to the interior surfaces of the unit. Sound absorbing material shall be held in place by a perforated mill finish galvanized liner to form a removable section easily inspected by maintenance personnel. The sound attenuation material and fastening system shall apply to the enclosure roof as well as side panels and doors as required to achieve a ___dBa sound rating when measured at a distance of ____ feet, free field.

Internal Wiring - All wiring within the enclosure shall be in conduits made from Rigid Metal, EMT, IMC, or liquid-tight material specifically manufactured for electrical use. All connections at the generator set shall be flexible, and all shall be provided and installed by Chillicothe Metal Co.

Interior Lighting (DC) - A battery operated light deriving its power from the engine DC circuit shall be installed in a strategic location within the enclosure and shall be controlled by a switch located by one of the entrance doors. The light shall be large enough to provide illumination in an emergency situation yet not such an overburdening drain will be placed on the starting batteries. The switch controlling this light shall be a wind-up timer type which automatically shuts off after a preset interval not to exceed one hour.

Interior Lighting (AC) - Two, forty-eight inch, dual-tube fluorescent lights shall be installed within the enclosure and strategically located on either side of the generator set. They shall be ceiling mounted and parallel to the length of the unit. Their AC power source shall be taken from the commercial power supply at the jobsite and wired-in by way of the load center specified elsewhere. The light switch box, located by one of the entrance way doors, shall have its own GFI protected duplex receptacle mounted therein for use by maintenance personnel.

Exterior Lighting - The enclosure shall be equipped with a light on the exterior of the building, wired into the commercial power supply load center, and activated automatically by way of a photoelectric cell which will switch the light on during evening hours and off during daylight hours. The fixture for the light shall be of vandalproof design.

Load Center - The enclosure shall be equipped with a load center as a single entry point for commercial power supply conduits and wiring by the installing contractor for the battery charger, jacket water heater(s), lighting, receptacles, etc., as specified and as shown on the drawings. The load center shall be mounted within the enclosure and allow for site condition conduit entry. The placement of this load center shall be shown on the submittal drawings. All internal wiring and conduit runs to the various ancillary equipment supplied with the package shall be pre-wired at the factory by CMCO in accordance with all governing codes pursuant to this application. The load center shall be considered as part of the emergency load and shall derive its power source downstream from the load transfer switch specified elsewhere. If a step-down transformer is required to be placed ahead of this load center, it, together with a properly sized protective device, shall be supplied and installed by CMCO within the enclosure.

Running Beacon - A weatherproof, flashing beacon light shall be mounted atop the enclosure and wired to operate off generator output voltage or battery voltage each time the generator runs. This beacon shall be amber in color.

Fault Beacon - A weatherproof, flashing beacon light and an audible alarm shall be mounted atop the enclosure and wired to operate off battery voltage in the event of an engine fault or alarm condition. This beacon will be red in color, and the siren shall be wired to the alarm silence switch in the generator control panel.

Oil & Water Drains - All necessary fittings, hoses, shut-off valves, etc., shall be provided by CMCO to facilitate lube oil and water drain at the exterior of the enclosure. In addition, engines equipped with crankcase breather tubes shall have this tube terminate at the exterior of the enclosure.

Enclosure Flooring - The floor of the enclosure shall be designed and constructed in such a manner as to prevent the entrance of rodents. This shall be accomplished with solid metal or “diamond plate” but, in any event, must be capable of fully supporting any ancillary equipment specified which may be secured to it plus the anticipated weight of maintenance personnel and their tools.

Skin Cooling - Under no circumstances shall the floor area or any of its parts be considered for cooling air intake or discharge requirements of the generator set or its associated equipment, nor shall its properties as a “heat sink” or heat dissipating medium be utilized in any manner whatsoever in this application.

FUEL SYSTEM:

Base & Mounting - The generator set and enclosure shall be mounted and shipped to the engine dealer on the structural steel sub-base as designed and manufactured by Chillicothe Metal Co. Provisions for crane unloading of the complete package shall be designed into the base of the unit.

Clearance - The base and enclosure assembly shall allow room within the package to mount and maintain the specified battery charger, engine starting batteries, racks and cables, main line circuit breaker, engine-generator control panel, and other items as specified or as shown on the drawings.

Weight - The weight of the entire unit consisting of generator set, base, enclosure, and other specified items including all liquids (i.e., fuel oil, lube oil and cooling solutions) shall be calculated by the engine dealer utilizing manufacturer’s data. The base of the unit shall be designed and manufactured as a heavy duty, structural steel construction with four point lifting provisions to support the calculated weight. Details and manufacturer’s certification of the base construction shall be included with the drawings submitted for approval as well as all dealer weight calculations supported by manufacturer’s data.

Fuel Tank - The unit shall be equipped with a UL142  labeled in-base fuel tank of  ___________ gallon capacity and shall be supplied with a low fuel level alarm float switch, a high fuel level alarm switch and a lockable fill cap. The normal fuel tank vents shall be extended through the roof of the enclosure and terminate with a vent cap at a point that measures at least 12-feet above grade. The emergency vent shall be located inside the enclosure at terminated with a spring load pressure release vent cap. All necessary fuel lines for proper engine performance shall be provided as well as a means to readily detect the fuel level in the tank without the use of a measuring stick. The unit shall be equipped with a fuel containment basin with a normal capacity of 120% of the fuel tank and shall be supplied with a leakage detector float switch in the basin.

EXHAUST SYSTEM:

Exhaust Silencer – An exterior mounted side inlet, end outlet, critical/hospital location type exhaust silencer and flexible, stainless steel exhaust bellows properly sized shall be furnished and installed according to the manufacturer’s recommendations by the enclosure manufacturer. Mounting of the silencer at the jobsite shall be by the installing contractor when the silencer is loose-shipped due to height restrictions in transit. The silencer shall be mounted such that its weight is not supported by the engine nor will exhaust system growth due to thermal expansion be imposed on the engine. Exhaust pipe sizes shall be sufficient to ensure that exhaust back pressure does not exceed the maximum limitations specified by the engine manufacturer. So called “spiral” and/or truck mufflers are disallowed and will not be considered.

(Optional Interior Silencer) An interior mounted low profile, internally insulated exhaust silencer and flexible, stainless steel exhaust bellows properly sized shall be furnished and installed according to the manufacturer’s recommendations by the enclosure manufacturer. The silencer shall be mounted such that its weight is not supported by the engine nor will exhaust system growth due to thermal expansion be imposed on the engine. Exhaust pipe sizes shall be sufficient to ensure that exhaust back pressure does not exceed the maximum limitations specified by the engine manufacturer. Insulation blankets shall be provided for the stainless steel flex and exhaust elbow assemblies located inside the enclosure.

Exhaust Outlet - Each silencer shall be fitted with a 90 elbow terminating in a vertical position and shall be fitted with a weighted rain cap.

Rain Skirt - At the point where the exhaust pipe penetrates the roof of the enclosure, a suitable “rain skirt” and collar shall be provided by CMCO. It shall be designed to prevent the entrance of rain yet allow for expansion and vibration of the exhaust piping without chafing or stress to the exhaust system.

STARTING SYSTEM:

Batteries - A lead acid storage battery set of the heavy duty diesel starting type shall be provided. Battery size shall be BCI Group No. 8D minimum, and shall be rated not less than 220 amp hours. Necessary cables and clamps shall be provided. Engines equipped with dual starting motors shall have dual battery banks.

Battery Tray - A battery tray shall be provided for the batteries and shall conform to NEC 480-7 (b). It shall be constructed and so treated as to be resistant to deterioration by battery electrolyte. Further, construction shall be such that any spillage or boil-over of battery electrolyte shall be contained within the tray to prevent a direct path to ground. A separate tray shall be provided for each battery bank and placed on each side of the engine on all dual starter motor equipped units.

Battery Charger - A current limiting, automatic DC battery charger shall be furnished to automatically recharge the batteries. Charger shall float at 2.17 volts per cell and equalize at 2.33 volts per cell. It shall include overload protection, silicon diode full wave rectifiers, voltage surge suppresser, DC ammeter, DC voltmeter, and have both AC and DC circuit breaker protection. The float and equalize rates of the charger shall be potentiometer adjustable in the field. The output current shall limit at 110% of full load and shall have ¼ of 1% regulation with a 10% AC line fluctuation. The enclosure shall be sealed and gasketed, dripproof aluminum cabinet. Amperage output shall not be less than ten (10) amperes. The charger shall be mounted and hard wired within the generator set enclosure by CMCO.

WIRING AND CONNECTIONS:

Wiring - All conduits, wire, cables, interconnections, etc., entering or exiting the generator enclosure shall be furnished and installed by the installing contractor. All wiring shall be in conduits sized in accordance with the NEC. All power wiring shall be THW copper. All control wiring shall be standard type THHN-THWN copper. All power and control wiring shall be installed for a complete and operating system.

WARRANTY:

Warranty - Equipment furnished under this Section shall be guaranteed against defective parts and workmanship under the terms and conditions of the manufacturer’s and dealer’s standard warranty. But, in no event shall it be for a period of less than one year from date of initial star-up of the system and shall include labor and travel time for necessary repairs at the jobsite. Submittal start-up data received without written warranties as specified will be rejected in their entirety.

END OF SECTION